Mini-PVA Totalp

Bifacial PV Analysis at a High-Alpine Site

Group 1 – Very Steep Ground Inclinations (HN ≥ 20°)

# 1. Project Overview

The Mini-PVA (Mini Photovoltaic Array) at Davos Totalp is a miniaturized bifacial PV test installation located at 2480 m a.s.l. (N46.838°, E9.813°). The system automatically cycles through different mechanical configurations, measuring power output of front and back sides of both a front and back module row.

The analysis covers 180 measurement days from October 2024 to March 2025. Group 1 focuses on very steep ground inclinations (HN ≥ 20°), which are particularly relevant for alpine terrain installations.

Configuration parameters:

- RA (Row spacing): 115 – 719 mm

- MN (Module tilt angle): 10 – 90° absolute

- HN (Ground slope): 0 – 40°

# 2. Methods

## 2.1 Data Processing

Raw measurements from 180 daily CSV files were combined and cleaned. Key data processing steps included:

- Timezone localisation with DST handling (27.10.2024 transition: 8 ambiguous rows dropped)

- MN overflow correction: unsigned 16-bit integer overflow (e.g. 65516 → −20°, subtract 65536)

- Removal of night/safe-position readings (MN = 0: 7936 rows)

- STC normalisation: Pnominal = Pmpp / P_STC for cross-channel comparability

- Day-wise interpolation of environmental data (prevents overnight bridging)

## 2.2 Yield Calculation

Daily yield [Wh/Wp] was computed by trapezoidal integration of Pnominal over time, restricted to daylight hours (solar elevation > 0°, calculated via pvlib). Bifacial yield combines front and back daily integrals:

Y_bif = Y_front + 0.9 × Y_back  [Wh/Wp]

The bifaciality factor of 0.9 is specified in the project assignment. Front and back are integrated separately before combining, which is physically correct since channels are measured sequentially (~1 s apart).

## 2.3 POA Irradiance & Regression Model

Plane-of-Array (POA) irradiance was calculated via pvlib's get_total_irradiance() function for each MN value, using DHI estimated as max(GHI − DNI × cos(zenith), 0). A Gradient Boosting Regressor was trained to predict yield for unmeasured configurations.

# 3. Key Results

## 3.1 Performance Map – Available Configurations

Due to the measurement schedule, only a subset of configurations had ≥ 5 measurement days for HN ≥ 20°:

| HN [°] | MN [°] | RA [mm] | Best total yield [Wh/Wp] | Best daily yield [Wh/Wp/day] |
| --- | --- | --- | --- | --- |
| 20° | 40° | 205 | 497.6 | 4.65 |
| 20° | 70° | 205 | 484.4 | 4.53 |
| 30° | 30° | 137 | 504.0 | 4.71 |
| 30° | 60° | 137 | 480.9 | 4.49 |
| 40° | — | — | Insufficient data (< 5 days) | — |

## 3.2 Optimal Module Tilt at Steep Ground Slopes

The main finding is that flatter module inclinations are optimal at steep ground slopes. At HN = 20°, MN = 40° gives the best yield; at HN = 30°, MN = 30° is optimal.

Physical explanation: The ground slope itself already contributes effective tilt toward the sun. An additional high module tilt overcorrects and reduces the angle of incidence on direct radiation, especially at low winter sun angles (~20° maximum elevation in November at N46.8°).

## 3.3 Row Spacing Effect

Larger row spacing (RA) consistently increases bifacial yield due to reduced inter-row shading, particularly of the back side. The effect is strongest at small spacings:

- RA = 115 mm → 477.9 Wh/Wp (HN=20°, MN=40°, front row)

- RA = 205 mm → 497.6 Wh/Wp (+4.1% improvement)

- Effect diminishes at larger RA values

## 3.4 Back-Side Contribution (Bifaciality)

The back side contributes approximately 25–35% of total bifacial yield. This is amplified at this alpine site due to high snow albedo — reflected radiation on the back side is significantly higher than at lower-altitude installations. Example for October 2024:

- Front row, HN=30°, MN=30°: total bifacial 122.4 Wh/Wp vs. front-only 92.0 Wh/Wp (+33%)

## 3.5 Seasonal Trend

Daily yield follows the expected winter pattern: declining from October toward the December solstice, then recovering toward March. The alpine site shows characteristic variability driven by cloud cover (quantified via 2-min GHI rolling standard deviation).

## 3.6 POA Irradiance

Calculated via pvlib for south-facing modules (azimuth = 180°):

| MN [°] | Total POA [Wh/m²] | Relative to MN=30° |
| --- | --- | --- |
| 30° | 61,368 | reference |
| 40° | 65,050 | +6.0% |
| 60° | 67,799 | +10.5% |
| 70° | 66,782 | +8.8% |

MN = 60° receives the most in-plane irradiance over the winter period. However, the measured bifacial yield peaks at lower MN values due to the steep ground slope effect described above.

## 3.7 Regression Model

Two regression approaches were tested using a Gradient Boosting Regressor:

| Model | Training data | R² | Limitation |
| --- | --- | --- | --- |
| Section 15 | 12 aggregated totals | N/A (too few) | Too few training points for cross-validation |
| Section 15b | 1260 daily yields | 0.942 | POA_day = 98% feature importance → captures weather, not config effect |

The high R² of 0.94 reflects the model learning that more solar irradiance produces more yield — not the configuration-specific differences. For robust extrapolation to unmeasured configurations, a broader measurement dataset would be required.

# 4. Conclusions

- At steep alpine slopes (HN ≥ 20°), flatter module inclinations (lower MN) are optimal, because the terrain itself contributes effective tilt.

- Larger row spacing consistently increases bifacial yield; the gain is ~4% from RA = 115 to 205 mm at HN = 20°.

- Back-side contribution is 25–35% of total bifacial yield — significantly enhanced by alpine snow albedo.

- HN = 40° could not be reliably analysed due to insufficient measurement days (< 5).

- The regression model confirms that day-to-day weather variation (POA) dominates over configuration differences in the current dataset.